Commercial Water Heating Solution

Written Specifications

SECTION 22 33 13.16 –

THERMOSTAT-CONTROL, INSTANTANEOUS ELECTRIC DOMESTIC WATER HEATERS

PRODUCT: PVI DURAWATT MINI

PART 1 – GENERAL

  - RELATED DOCUMENTS

- Drawings and general provisions of the Contract apply to this Section, including General and Supplementary Conditions and Division 01 Specification Sections.

1.2 	SUMMARY

This section includes electric water heaters for potable water

1.3 	REFERENCES

- UL 1453 “Electric Booster and Commercial Storage Tank Water Heaters”

- ASME Boiler and Pressure Vessel Code, Section IV, Part HLW

- NFPA 70 – National Electric Code

- NSF/ANSI Standard 61 – Drinking Water System Components

- NSF/ANSI Standard 372 – Drinking Water System Components – Lead Content

1.4 	SUBMITTALS

- Product Data: Include rated capacities; shipping, installed, and operating weights; furnished specialties and accessories for each model indicated.

- Shop Drawings: Detail equipment assemblies and indicate dimensions, required clearances, components, and size of each field connection.

- Wiring Diagrams: Detail for wiring power signal, differentiate between manufacture-installed and field-installed wiring.

- Maintenance Data: Include in the maintenance manuals specified in Division 1. Include maintenance guide and wiring diagrams.

1.5 	REGULATORY REQUIREMENTS

- Conform to applicable code for internal wiring of factory wired equipment.

- Units: ETL, UL, or CSA Listed as a Complete Electric Water Heater Assembly.

- Conform to ASME Section IV, Part HLW for Duplex Water Heater construction.

- Conform to NSF/ANSI Standard 372 – Drinking Water System Components – Lead Content

1.6 	QUALITY ASSURANCE

- Listing: The water heater will be ETL listed to UL 1453 “Electric Booster and Commercial Storage Tank Water Heaters”

- ASME Compliance: Water heater shall bear the ASME HLW stamp and be National Board listed.

- NSF/ANSI Compliance: Water heater shall conform to the NSF/ANSI 372 by a recognized certifying body.

- Manufacturer: Company specializing in manufacturing the products specified in this section with minimum twenty years’ experience.

1.7 	WARRANTY

- The online warranty for this product is located on PVI’s website (https://www.pvi.com/) and in the event that the terms or conditions of this specification conflict with the online warranty, the terms and conditions of the online warranty shall control.

- Pressure Vessel / Heating Chamber: 10-year coverage for manufacturing or material defects, leaks, the production of rusty water and or chloride stress corrosion cracking. Vessel warranty does not require inspection and maintenance of anode rods. The warranty shall begin at the date of installation.

- All other heater parts: 1 year

- The heater shall have a first-year service policy, which shall cover labor and freight costs under certain conditions for warranty covered services.

PART 2 – PRODUCTS

2.1 	MANUFACTURERS

- The water heaters shall be ETL listed as a complete unit. The heater shall satisfy current Federal Energy Policy Act standards for both thermal efficiency and standby heat losses.

- Manufacturers: PVI is the basis of design. Acceptable manufacturers shall be subject to compliance with the requirements.

2.2	CONSTRUCTION

- The storage section of the water heater shall be ASME HLW stamped, and National Board Registered for the maximum allowable working pressure of 150 psi and pressure tested at 1-1/2 times working pressure.

- Connection sizes shall be 1-1/2” NPT. Tank shall include a 3/4” NPT relief valve opening.

- The storage section of the water heater shall be an unlined pressure vessel constructed from phase-balanced austenitic and ferritic duplex steel with a chemical structure containing a minimum of 21% chromium to prevent corrosion and mill certified per ASTM A 923 Methods A to ensure that the product is free of detrimental chemical precipitation that affects corrosion resistance.

- Waterside surfaces shall be welded internally utilizing joint designs to minimize volume of weld deposit and heat input. All heat affected zones (HAZ) shall be processed after welding to ensure the HAZ corrosion resistance is consistent with the mill condition base metal chemical composition. Weld procedures (amperage, volts, welding speed, filler metals and shielding gases) utilized shall result in a narrow range of austenite-ferrite microstructure content consistent with phase balanced objectives for welds, HAZ and the base metal.

- All internal and external vessel surfaces shall undergo full immersion passivation and pickling processing to meet critical temperature, duration and chemical concentration controls required to complete corrosion resistance restoration of pressure vessel surfaces. Other passivation and pickling methods are not accepted. Immersion passivation and pickling certification documents are required and shall be provided with each product.

- The water heater shall be completely factory packaged within a single wall-mountable enclosure, requiring only job site wall-mounting, or floor-mounting with an acceptable floor-mounting leg kit, and hookup for electrical and plumbing.

- Pressure relief valve rated to 150 PSI shall be factory provided.

- Materials shall meet ASME Section II material requirements and be accepted by NSF 61 for municipal potable water systems. Pressure vessel materials shall contain more than 80% post-consumer recycled materials and be 100% recyclable.

- Water contacting vessel surfaces will be non-porous and exhibit 0% water absorption.

- Internally lined or plated storage tanks will not be acceptable.

- Water heaters that require anodes will not be acceptable.

- Heating elements for 12kW and 24kW units will be rated for 4 kW and 68 watts per square inch heat density. Heating elements for 30 kW and 45 kW units will be rated for 5 kW and 71 watts per square inch heat density. Heating elements for 18 kW, 36 kW, and 54 kW units will be rated for 6 kW and 84 watts per square inch heat density.

- Heating elements will be sheathed in Incoloy. Each element will individually thread into the pressure vessel by means of NPSM threads with an O-ring seal. A fused magnetic contactor will be supplied for the power circuit. Maximum current per circuit will be no more than 75 amps on three-phase units.

- The pressure vessel will not require anodes of any type and none will be used.

2.3 	WATER HEATER TRIM

- As a minimum, the heater will be equipped with the following:

- An electronic low water cutoff

- An immersion operating thermostat

- Immersion temperature limiting device

- An ASME rated temperature and pressure relief valve

- Operating and safety controls shall meet the requirements of UL 1453. Operating and safety controls shall meet the requirements of MASS code.

- The water heater shall employ an electronic operating control with digital temperature readout. Operator shall be capable of connecting to a building automation system through serial connection using Modbus RTU protocol.

PART 3 – EXECUTION

3.1 	INSTALLATION

Install water heaters level and plumb in accordance with manufacturers written instructions and referenced standards.

3.2 	FINISHING

The heater shall fit properly in the space provided and installation shall conform to all local, state, and national codes.

3.3	START-UP

Start up on the unit will be performed by factory trained and authorized personnel. A copy of the startup report will be provided to the owner.

END OF SECTION