Specification
Lead free* digital water temperature control and monitoring system shall feature full-color touchscreen interface which is configurable on location and does not require factory
pre-programming. System shall control water temperature to
±2°F in accordance with ASSE 1017 and resist “temperature creep” during periods of low/zero demand. The control shall be password protected and feature a user-adjustable outlet temperature range of 60°F to 180°F with high and low tem-perature alerts, and an approach temperature of 2°F.
System shall digitally control and monitor mixed outlet tem-perature. The control shall integrate with building automation systems (separate module not required) through BACnet and Modbus protocols and feature local and remote temperature alarms.
System shall provide monitoring and visibility of mixing valve assets across multiple locations/sublocations. System shall offer the ability to remote temperature control for admin levels. System shall be capable of sending system alerts by text and/or email and prioritizing alerts based on levels of safety and potential liability. System offers two user levels for security. The control shall be equipped with secure Wi-Fi protocols WPA2-PSK and WPA2-PEAP-MSCHAPv2.
System shall feature a user-set, high-temperature sanitiza-tion mode for thermal disinfection of bacteria and a pro-grammable temperature set back feature to improve energy efficiency. System shall also feature high speed actuator with override feature. In the event of a power failure, system
shall open full cold supply. In case of a loss of cold water, the system shall close hot water supply.
System shall be listed/approved to ASSE 1017, cUPC, NSF, UL 60730-1, UL 60730-2-9, IEC 60730.
System shall be an PVI DT2S075VL, DT2S100VL, DT2S150VL, or DT2S200VL.




WARNING
Hot water poses a danger of burning or scalding above 110 degrees Fahrenheit. Setting the mixing valve to temperatures over 110 Fahrenheit without the protection of additional point-of-use mixing valves could result in scalding at point-of-use fixtures such as faucets, sinks, tubs, and showers.
The Sanitizing function produces high temperature at all point-of-use fixtures and extreme care must be taken to mit-igate against the risk of personal injuries such as burning or scolding, or other property damage. The Sanitization function must only be used for the purposes of sanitizing the system, and never during normal operations or use.
Sanitation times and temperatures should be chosen based on your company's Sanitization Protocol requirements, your plumbing systems characteristics, and sanitation validation data.
Ensure proper time is allotted for proper cooldown of water system after sanitization in order for temperatures to return to normal. Not giving enough time for this cooldown period can also result in scalding at point-of-use devices.

WARNING
DigiTemp 2S system provides user-directed control and mon-itoring of water distribution systems. The Sanitization mode is intended for use as part of a user-directed, controlled,
and supervised protocol that has been safely and properly designed.
It is recommended to install the DigiTemp 2S system as part of a ASSE compliant water distribution system, including point-of-use mixing valves. Installation and adjustment of the DigiTemp 2S system are the responsibility of the owner and installer and must be done by qualified personnel in accor-dance with the manufacturer’s instructions, and complying with all governmental requirements, building and construction codes and standards. The owner and user of the DigiTemp 2S system are responsible for selecting and installing the product in an appropriate water distribution system, proper sizing, maintaining proper water quality/condition, and de-ciding what temperature is safe and appropriate for the water distribution users and facility.
Always read and follow Installation, Operation, and Main-tenance Manual and all product warnings and labels, and comply with all governmental and safety requirements.

NOTICE
A copy of the applicable limited warranty and disclaimers is available at pvi.com.
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